[image: image1.jpg]


[image: image1.jpg]

Specification for Portable Generators
	REVISION STATUS

	Rev
	Date 
	Description
	Revision by
	Checked
	Approved

	1
	17/09/09
	Issued
	M.Spinks
	F.Locke
	F.Locke

	2
	22/2/13
	Draft
	G.Conway
	
	

	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 


Anglo Coal (Dawson Management) Pty Ltd               
ABN 15 006 746 701

Dawson Highway, Moura, 4718.

Ph:   (07) 4990 9902  

Fax: (07) 4990 9800

All correspondence to:

PO Box 225, Moura, QLD, 4718.

Contents  
31
General Requirements


31.1
Purpose


31.2
Priority of Specifications


31.3
Reference to Australian Standards


32
Technical Specifications


32.1
Alternator


32.2
Engine


42.3
Engine Control Panel


42.4
Engine Protection


42.5
Engine Electrical System


42.6
Fuel Tank


52.7
Service Points


52.8
Fuel Monitoring


52.9
Frame Mounting


52.10
Trailer


52.11
Trailer Support Legs


62.12
Hydraulic Controls


62.13
Engine canopy


62.14
Statutory Approval


62.15
Electrical Systems


72.16
GPS Electronics


82.17
Schematics


82.18
Service Lighting


82.19
Fire Suppression


82.20
Steel/ Welding


82.21
Plant Number


82.22
Portable Generator Colours


93
Documentation


94
Maintenance


95
Warranty




1 General Requirements

1.1 Purpose

The purpose of this standard specification for Anglo Coal Dawson Management is to provide the minimum requirements relating to the construction and delivery of transportable generators to site. 
1.2 Priority of Specifications

In addition to the requirements of this specification, equipments shall comply with latest relevant Australian Standards, applicable Mining Acts and Statutory Regulations, and other related ACA Standard Specifications. In the event that the requirements are not consistent, the higher of the standards shall be followed. 
1.3 Reference to Australian Standards
AS 3000 Electrical Installations (known as Australian/New Zealand wiring rules);

AS 3007 Electrical Installations – Surface Mine & Associated Processing Plant;
AS 3713 Noise Level Emissions;
AS 1170.2 Wind Loading Criteria;
AS 1101.3 2005 Graphic Symbols for general engineering – Welding and non destructive examination;
AS 1554.1 2004 Structural Steel Welding – Welding of Steel Structures;
AS 2203-1981 Carbon Steel electrodes, cored (for arc welding);
AS 2717.1-1996 Welding – Electrodes – Gas Metal Arc – Ferritic steel electrodes.
2 Technical Specifications
2.1 Alternator

Portable generators used for the provision of general power shall be supplied with a “Stamford”, 37 KVA, 415 Volt, 3 phase, 50 Hz, double bearing, direct coupled, four poles, revolving field alternator or an agreed equivalent. The alternator shall be anti vibration mounted.
Alternative alternators to suit particular applications, shall be approved by the EEM.
2.2 Engine

The engine of portable generators used for the provision of general power shall be a “Kubota” V2203 engine liquid cooled naturally aspirated diesel engine producing 20.3 Kilowatts continuous at 1500 RPM or an agreed equivalent. The Cooling system shall be filled with TEC PG XL coolant.
Alternative engines to suit particular applications, shall be approved by the EEM.
In addition the engine shall be fitted with the following equipment.
- ‘Donaldson’ heavy-duty air cleaner and pre cleaner.

- Sound control muffler.

- ‘Wiggins’ oil fill / evacuation and an extended dipstick.

2.3 Engine Control Panel

The control panel shall be housed within a sealed box with clear hinged lid and be fitted with the following equipment.

- Key start ignition with lockout device

- Hour meter

2.4 Engine Protection

The engine shall be protected from damage through the inclusion of a protection system. The protection system shall contain the following.

- Low water protection

- High temperature protection – Cat 7N9785 switch

- Low oil pressure protection – Cat 107.0611 switch

- PLC based controller

2.5 Engine Electrical System

The engine electrical system shall be a 12 volt start and charge system. The engine electrical system shall be powered by one 12 volt “CAT” heavy duty battery (part number 1535720) fitted within a vented, fabricated steel battery box. The battery box lid is to be non conductive or unable to come into contact with the battery terminals under normal operating and maintenance conditions.
The 12 Volt electrical system shall be fitted with the following equipment.
- Circuit breakers in place of fuse holders

- All wiring part of the 12V engine electrical system shall be protected by Adaptaflex PAF21 conduit.
- Battery isolator switch with lockout device (LockSafe device, part number LS 11001-01) providing positive pole isolation.
- Ashdown jump-start receptacle (part number 6594350).
- Emergency stop button to be mounted next to Wiggins fill point.
- Two (2) fully adjustable rubber body 12 Volt sealed beam floodlights (Hella Matador with covers, Part Number 1511) for night work.

- Supplied wiring diagram.
2.6 Fuel Tank

The fuel tank shall be fabricated from plate and give the plant a minimum of 4 x 12 hour shift operations when run at 75% load. The fuel tank is to be fitted with an overflow valve or be constructed in such a manner as to ensure that fuel cannot be directed onto the battery or 415V AC distribution system, operator area, or service point area.
2.7 Service Points

The fuel tank shall be fitted with a Wiggins fuel fill pipe and Wiggins Engine oil fill point. The service points shall be located on the control panel side of the generator. The fuel tank shall additionally be fitted with a manual fill pipe and a vent. 
2.8 Fuel Monitoring

A sight level gauge shall be provided to monitor the level of the fuel in the fuel tank. 

2.9 Frame Mounting

Fabrication shall be of a suitable quality to meet the onsite conditions. All manufacturing shall comply with the relevant Australian Standards.
2.10 Trailer

Portable generator shall be mounted on or constructed into a heavy duty tandem axle trailer fitted with Land Cruiser wheels and rims (750 x 16). Trailer axle suspension shall be of leaf spring type. All axles are to be fitted with mechanical override disc brakes.

A drawbar shall be fitted to one end of the trailer and be fitted with jug handles and safety chains. Trailer shall be fitted with one heavy duty tow rope hitch.
Rubber mudguards shall be fabricated and bolted to the trailer frame and hang down sufficiently to prevent rocks being flicked up into fittings.

Trailer shall be sandblasted, primed and industrially painted.

Trailer is to be labelled with two (2) signs reading “To be towed as per site procedures” on each side near tow hitch.

The trailer shall arrive onsite road registered. Registration shall remain valid until 07/10/Year (7th of October). Tail lights are to be of LED type.
A Hydraulic Breakaway system shall be fitted to the portable generator.

2.11 Trailer Support Legs

Trailer shall be fitted with four (4) hydraulic support legs located at each corner of the trailer. The support leg pads on each leg shall be circular and a minimum of 30cm diameter or an alternate agreed area and shape. 
Reflective tape shall be fitted along the outside of each leg.

Each support leg shall be fitted with one (1) pressure switch with LED Mimic to indicate which support leg is not loaded. Pressure switches shall be located to provide easy access during maintenance and repair, but sufficiently protected from accidental damage during operation and transport.

Four (4) chock boards shall be supplied with holding brackets for storage of chocks.

2.12 Hydraulic Controls

- Hydraulic control valves shall be mounted on the passenger side of the plant. All controls clearly labelled. Labels to include which direction results in which motion.

- Spirit level indicator to show level ground. Indicator shall be of bull’s eye type and fitted at the operators controls.

- All hydraulic lines shall be double wire braided and fitted with J.I.C. fittings. All hydraulic lines are secured using bolt on clamps.

- No pinch points for the main electrical cables or hydraulic hoses between mast structure and mast pivot point.

2.13 Engine canopy

Engine canopy shall be fabricated from R/H/S and sheet steel and fitted as standard providing protection to and fully enclosing the engine, radiator and alternator. 
Canopy shall be fitted with a top hinged, doors providing internal access to the full length of both sides of the portable generator. Doors shall be fitted with gas struts and padlockable ‘L’ handles. Canopy shall be fitted with removable top panel to allow removal of all internal components including but not limited to the engine and alternator. 
Four (4) certified lifting lugs shall be fitted to the top of the portable generator frame capable of four point slinging. Plant shall be labelled with the gross weight of the plant with full capacity of all fuels, lubricants and coolants. Labels shall be located on each side of the plant (one label per side), in a clearly visible location when accessing lifting lugs.
2.14 Statutory Approval

All electrical components shall be fitted and wired by a qualified electrician to meet Queensland Mining Act Regulations. The portable generator shall be built to the standards including but not limited to the following Australian Standards.

AS 3000 Electrical Wiring Rules

AS 3007 Electrical Installations – Surface Mine & Associated Processing Plant

AS 3713 Noise Level Emissions
AS 1170.2 Wind Loading Criteria

2.15 Electrical Systems

The electrical system shall meet the following requirements.
The main AC electrical supply provided by the alternator shall be protected by a circuit breaker fitted with an adjustable 30-100mA Residual Current Device (RCD) with a testing facility. Each power circuit shall be protected by an individual circuit breaker with 30mA residual current protection. Any 240V AC power outlets shall be over current and earth leakage protected by individual circuit breakers with 30mA residual current devices. Circuit breakers shall be accessible without the use of a tool.
The electrical system shall be protected by a voltage regulator ensuring that the electrical system maintains 415V in 3 phase configuration and 240V in single phase configuration.
The electrical system shall be 50Hz only and any selection devices that can change the system to another frequency shall be disabled or removed.
The portable generator shall be fitted with the following instrumentation.
One (1) ammeter for monitoring current draw in each phase from the alternator. The ammeter shall be provided with a selector switch to indicate which phase is being displayed.
Three (3) voltmeters for monitoring the voltage levels at the alternator. Each phase shall have a dedicated voltmeter.

Portable generators used for the provision of general power shall be fitted with the following items.  These requirements may be waived be the EEM, to suit the particular application.
· One (1) 415V, 90A, 3 phase + N + E weatherproof socket outlet. (Marechal DS6 90amp outlet part numbers 3168017+316A013)
· One (1) 240V, 1 phase 3 pin weatherproof socket outlet. 240V

· One (1) selector switch to change between each outlet. The selector switch shall provide interlocks on the outlet circuits to ensure only one socket is ever supplied at any time.
All cables supplying the main 415V/240V AC system shall be encased within Liquidtite conduit featuring a metal mound interior with PVC outer coating. Cable ties shall not be used for securing cables. Additional mechanical protection shall be provided where required.
All electrical enclosures shall be a minimum of IP56 except where otherwise stated.

Flexible earthing straps shall be fitted across all rubber mounts separating conductive material and in any other location required to ensure equipotential bonding.
The portable generator shall maintain continuity with earth through the means of an earth electrode complying with AS3000. The earth electrode shall be marked at 1.2m to indicate the required earthing depth. The portable generator shall be fitted with a means of securing the earth electrode during transport.

All electrical wiring shall be terminated at each end by suitable electrical lugs and shall have wire labels fitted to each end of each wire.

All electrical devices shall be individually labelled. Labels shall be easily visible and located within a suitable distance of the device being described. Labels shall be attached by screws.
2.16 GPS Electronics

The plant shall be fitted with a Tait TM8000GPS KIT available from Nixon Communications. The kit shall contain a Tait Radio, antenna, mounting cradle, power cable, GPS Receiver/antenna, Hi-speed data modem, ignition sensor, or an agreed equivalent configuration. The GPS system shall be able to determine and transmit the plant’s location and ignition status via the pre-existing UHF frequency used onsite. The radio unit and modem shall be installed with a firmware and software version compatible with the system used onsite.

All components requiring protection against the ingress of water and dust shall be housed within a stainless steel enclosure with an IP66 rating. All connections made to the 12 volt electrical system shall be protected by a double pole circuit breaker as per section 2.15 Electrical Systems.

2.17 Schematics

Electrical schematics shall be submitted to the Anglo Coal Dawson Management Electrical Engineering Manager for approval prior to construction.
2.18 Service Lighting

Service lighting shall be provided as per section 2.5 Engine Electrical System.
2.19 Fire Suppression
Each portable generator shall be fitted with two (2) 4.5kg Dry Chemical Powder Fire Extinguishers complete with quick release vehicle brackets. The extinguishers are to be mounted on opposite outside side panels of the portable generator in easily accessible locations that are protected from accidental damage.
2.20 Steel/ Welding

Weld details, welding procedures and inspection requirements shall meet the requirements of Australian Standards AS 1101.3 2005; AS 1554.1 2004; AS 2203-1981; AS 2717.1-1996.

2.21 Plant Number

Plant number (to be advised by Anglo Coal Dawson Management) shall be of a minimum of 100mm height and clearly displayed on both sides of the portable generator. The plant number shall be coloured reflective yellow on a black background.
2.22 Portable Generator Colours

The Portable Generator shall meet the requirements of the following colour scheme.

Chassis & Canopy 

White

Mudguards


White

Engine



White or standard oil impregnated

Alternator


Orange or standard oil impregnated

Plant Number
Reflective Yellow text, Black background as per section 2.22 Plant Number



3 Documentation

The following documentation shall be provided upon delivery (except where otherwise stated) of the plant to site.
2 parts book sets for each plant delivered to suit the specific plant (to be supplied to site prior to delivery of plant to site as per section 4. Maintenance). Parts book shall also be supplied in electronic PDF. A ‘Link One’ format of the parts list should also be provided if available.
2 service manuals for each plant delivered. Service manual shall also be supplied in electronic PDF format.
Wiring diagram of 12 volt electrical system laminated on A3 size paper drawn to the appropriate Australian Standard.

Electrical schematic (approved prior to construction as per section 2.16 Schematics).
All drawings including wiring diagrams and schematics shall be supplied in printed format, electronic CAD format, and electronic PDF format.

4 Maintenance

A lubrication and maintenance schedule suitable to the Portable Generator shall be provided. Lubrication type and quantities shall be documented and provided.

 A comprehensive consumable parts list shall be provided before delivery. A listing of all major components stating Serial number, brand, model and any other special instructions shall be included in the supplied documentation. For electrical parts, this shall include OEM name and part number as well as reference part number.
5 Warranty

A full warranty statement shall be supplied and agreed upon by Anglo Coal Dawson Management. 

	Specification for Portable Generators.doc
	Last printed 22/02/2013 1:52:00 PM
	i



[image: image2.png]Real Mining. Real People. Real Difference.



