| Equipment Owner or Responsible Person |  | Equipment Type/Make/Model/Shape |  | Call Sign/Equipment ID |  | Registration Number |
| --- | --- | --- | --- | --- | --- | --- |
| Company the inspection is conducted for |  | Inspected by (print) |  | Inspection Company |  |  |
| Declaration Submitted | Towing Capacity | Meter Reading | First Inspection |  | Annual Inspection |  |
| Yes No |  |  | Random Inspection |  | Re-Inspection |  |

|  | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Electrical Labelling |  |  |  |
| Maximum voltage above ELV within the enclosure Sign |  |  |  |
| Signs on any cover or door which exposes live conductors |  |  |  |
| IEC/AS 60974-1 Compliance plate or compliance certificate for machine serial & model number |  |  |  |
| Protection |  |  |  |
| The minimum degree of protection against access to live parts shall be IP2X |  |  |  |
| All electrical conductors terminated correctly, secured and effective as per AS3000 |  |  |  |
| VRD installed. The reaction time for the VRD to reduce the voltage to the low voltage state after the circuit resistance reaches or exceeds 200 Ohms shall be less than 300 ms |  |  |  |
| All welding equipment shall have an RID |  |  |  |
| Lockable isolation of electrical energy when inspection, repair or maintenance is being carried out |  |  |  |
| Segregation of ELV and LV |  |  |  |
| The LV cables are double insulated |  |  |  |
| All cable or each conductor of a multi-core cable are insulated to the highest voltage |  |  |  |
| The LV cables are physically separated from the ELV cables by suitable continuous barriers |  |  |  |
| Welders |  |  |  |
| Use of DC welding machines is preferable |  |  |  |
| Welding machines must have a degree of protection of IP23 for outdoor use and IP21 for dry indoor use |  |  |  |
| The casing of mains powered inverter welding machines are required to be constructed entirely of non-conductive materials |  |  |  |
| equipment shall be free from mechanical or heat damage |  |  |  |
| Welding lead Connections shall not be frayed and shall be firmly attached. Insulation and leads must be in good condition. Any repairs made to the sheath must be rectified with heavy duty heat shrink or rubber sealing tape, not standard electrical taped. Maximum of 3 lead repairs permitted. |  |  |  |
| Welding leads not to exceed 9 m in length. |  |  |  |
| Preferred that no GPOs be installed. However, if there is GPOs Earth leakage must be on. each circuit. |  |  |  |
| GPO outlets must operate at 50Hz |  |  |  |
| GPO outlets with low idle must have a system to disconnect the outlets when the machine is not switched to high idle |  |  |  |
| The rating plate shall be placed in a practical and visible location and have all applicable information |  |  |  |
| Output connections for the attachment of the work piece or electrode must be appropriately identified and in good condition |  |  |  |
| General |  |  |  |
| Electrical enclosures and panels must be locked or require a tool to gain access to live conductors. |  |  |  |
| Bushings on any cable that passes through a metallic structure |  |  |  |
| All Earth cable to be green and yellow |  |  |  |
| Relevant Circuit Diagram |  |  |  |
| Confirm any electrical leads have test-tag in date (elec licence # must be legible) |  |  |  |

| Result of Inspection | Pass: | Yes No | Follow up inspection required: | Yes No |  |
| --- | --- | --- | --- | --- | --- |
|  | Sticker Issued (circle) | Green Orange | Sticker number: |  | Expiry date / / |
| Comments or details of repairs needed |  |  |  |  |  |

I certify that this report is a true record of the equipment’s compliance.

Signature (Inspector):		Date: 		Location of Inspection: