| Equipment Owner or Responsible Person |  | Equipment Type/Make/Model/Shape |  | Call Sign/Equipment ID |  | Registration Number |
| --- | --- | --- | --- | --- | --- | --- |
| Company the inspection is conducted for |  | Inspected by (print) |  | Inspection Company |  |  |
| Declaration Submitted | Towing Capacity | Meter Reading | First Inspection |  | Annual Inspection |  |
| Yes No |  |  | Random Inspection |  | Re-Inspection |  |

|  | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Protection |  |  |  |
| All electrical Enclosures must be locked or require a tool to gain access to live parts |  |  |  |
| The minimum degree of protection against access to live parts is IP2X |  |  |  |
| The supply to every electrical installation shall be controlled on the main switchboard by a main switch or switched that control the whole of the electrical installation. Where multiple supplies are provided, each supply shall be controlled by a main switch or switched on the main switchboard for each supply. |  |  |  |
| Before the escutcheon is opened, check that the main switch board has: Electrical Interlocking to trip the main switch, or Mechanical interlocking to main switch must be in the off position, or Requires a key or tool to open the escutcheon with warning labels applied. |  |  |  |
| The live side of the main switch, which can be accessible with the escutcheon open, shall be protected to IP2X |  |  |  |
| Each outgoing circuit shall have overcurrent protection. The rating of the O/C device must be at least equal to the prospective fault current. |  |  |  |
| Fluorescent light switches shall be suitably rated for the load |  |  |  |
| Confirm all final sub-circuits are protected by 30mA E/L. |  |  |  |
| As per AS3000.2.6.2.2 RCDs shall have dual pole switching |  |  |  |
| Equipment utilising a switch mode power supply must have a robust earth connection. Screw type connection only acceptable (not spade or spring clip type) |  |  |  |
| All conductive parts of the equipment must be provided with an equipotential bond of suitable size for mechanical robustness. Enclosure doors containing electrical apparatus shall be bonded using a suitably sized earth conductor |  |  |  |
| Segregation of LV and ELV |  |  |  |
| The LV cables are double insulated |  |  |  |
| All cable or each conductor of a multi-core cable are insulated to the highest voltage |  |  |  |
| The LV cables are physically separated from the ELV cables by suitable continuous barriers |  |  |  |
| Confirm No voltages above 55v to earth leave an enclosure (eg. Pendant controls) |  |  |  |
| Control Voltage |  |  |  |
| All operator interfaces to be ELV |  |  |  |
| General |  |  |  |
| Check that the switchboard is not located within 1.2m of the ground/floor/platform |  |  |  |
| All outlets shall be positioned to allow ease of connection, removal of plugs, adequate bending radius of cables and ready access to outlet controls |  |  |  |
| Any switchboard shall be located so that access is not obstructed by the structure and has adequate space on all sides to provide safe access to electrical contents. |  |  |  |
| Any cable that passes through a metallic structure shall be adequately bushed to minimise abrasion. |  |  |  |
| IP Ratings of switchgear, outlets, and other Plant shall be a minimum of IP56 unless otherwise approved by the EEM or their delegate. |  |  |  |
| Plant shall be installed in accordance with the Wiring Rules AS3000. |  |  |  |
| Confirm Circuit breakers are all lockable |  |  |  |
| Confirm any electrical leads have test-tag in date (elec licence # must be legible) |  |  |  |
| Copies of the Electrical schematics must be available & legible |  |  |  |
| Cabling are to be coloured as follow: 415V AC Power: red, white, blue 240V AC Power: red 415/240V Neutral: black 110V control: white Earth: green and yellow |  |  |  |
| Before making the equipment live, carry out a visual inspection of all electrical apparatus and associated equipment, checking that all items of electrical equipment and their mechanical supports have been securely mounted, are plumb and that no corrosion of metal parts is evident, all enclosures, covers and doors are secured and all padlocks fitted as applicable |  |  |  |
| Signage |  |  |  |
| Plant and fixed switchgear shall be fitted with a sign advising on the procedures to be undertaken in the event of a fire. |  |  |  |
| Plant and switchgear shall be fitted with a label warning of the dangers of electricity, the level of voltage present on the equipment, and isolate elsewhere signs on enclosure covers. |  |  |  |
| All fixed switchgear shall be fitted with a sign showing how to carry out resuscitation after an electric shock. |  |  |  |
| Fixed switchgear shall be fitted with a sign identifying the Plant or system supplied by the switch. |  |  |  |
| Tests |  |  |  |
| Earth Leakage Test sheet must be suppled confirming that all E/L protection devices have passed Injection Testing |  |  |  |
| IR test All live parts of an electrical installation shall not be less than 1M ohm. Note: Sheathed heating elements of appliances, RCDs with a functional earth connection and some other electrical equipment may cause test results lower than 1M ohms. These should be disconnected from the circuit prior to testing. An acceptable IR value for sheathed heating elements is 0.01M ohms |  |  |  |
| Earthing of Equipment test The resistance of the main eathing conductor shall not be more than 0.5 ohms. The max resistance to any other earth point shall not be greater than 1 ohm. |  |  |  |
| Polarity tests Active and neutral conductors have not been transposed. Socket outlets polarity correct. All neutral conductors connected to the neutral bar. |  |  |  |

| IR test Equipment Details and Serial Number |  | Earth Test Results | Reading Ω |
| --- | --- | --- | --- |
|  |  | Main Earth |  |
|  |  | Neutral Link (TN/MEN) |  |
| IR to Earth/Frame Location | Resistance M Ω | Bonding Location | Reading Ω |

| Result of Inspection | Pass: | Yes No | Follow up inspection required: | Yes No |  |
| --- | --- | --- | --- | --- | --- |
|  | Sticker Issued (circle) | Green Orange | Sticker number: |  | Expiry date / / |
| Comments or details of repairs needed |  |  |  |  |  |

I certify that this report is a true record of the equipment’s compliance.

Signature (Inspector):		Date: 		Location of Inspection: