| Equipment Owner or Responsible Person |  | Equipment Type/Make/Model/Shape |  | Call Sign/Equipment ID |  | Registration Number |
| --- | --- | --- | --- | --- | --- | --- |
| Company the inspection is conducted for |  | Inspected by (print) |  | Inspection Company |  |  |
| Declaration Submitted | Towing Capacity | Meter Reading | First Inspection |  | Annual Inspection |  |
| Yes No |  |  | Random Inspection |  | Re-Inspection |  |

|  | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Electrical Labelling |  |  |  |
| Maximum voltage above ELV within the enclosure Sign |  |  |  |
| Signs on any cover or door which exposes live conductors |  |  |  |
| Protection |  |  |  |
| The minimum degree of protection against access to live parts shall be IP2X |  |  |  |
| All electrical conductors terminated correctly, secured and effective as per AS3000 |  |  |  |
| The main AC electrical supply provided by the alternator shall be protected by a circuit breaker fitted with an adjustable 30-100mA Residual Current Device (RCD) with a testing facility |  |  |  |
| Each power circuit shall be protected by an individual circuit breaker with 30mA residual current protection. Any 240V AC power outlets shall be over current and earth leakage protected by individual circuit breakers with 30mA residual current devices |  |  |  |
| Each lighting fixture shall be protected by a lockable individual circuit breaker with 30mA residual current protection |  |  |  |
| 3 pin earth leakage injection testing facility either added onto the main switchboard or in a separate enclosure |  |  |  |
| Lockable isolation of electrical energy when inspection, repair or maintenance is being carried out |  |  |  |
| Segregation of ELV and LV |  |  |  |
| The LV cables are double insulated |  |  |  |
| All cable or each conductor of a multi-core cable are insulated to the highest voltage |  |  |  |
| The LV cables are physically separated from the ELV cables by suitable continuous barriers |  |  |  |
| Lighting Plant |  |  |  |
| Lighting Plant shall be equipped with an alternator capable of providing enough power for the lighting plant. The alternator shall be anti-vibration mounted. |  |  |  |
| The engine shall be a liquid cooled naturally aspirated diesel engine. |  |  |  |
| Fuel tank to be large enough to supply 4x12 hour shift operations |  |  |  |
| Sight level fuel gauge installed |  |  |  |
| Engine shall be fitted with a Sound control muffler |  |  |  |
| Engine Protection |  |  |  |
| Low water protection |  |  |  |
| High temperature protection |  |  |  |
| Low oil pressure protection |  |  |  |
| The 12 Volt electrical system |  |  |  |
| The engine electrical system shall be a 12 volt start and charge system. |  |  |  |
| The engine electrical system shall be powered by one 12 volt heavy duty battery fitted within a vented, fabricated stainless steel battery box |  |  |  |
| Battery isolator switch with lockout device providing positive pole isolation |  |  |  |
| Electrical System |  |  |  |
| AC power outlets will also have a minimum rating of IP56 |  |  |  |
| All cabling should be V90 or higher |  |  |  |
| A time clock and bypass switch shall be connected to the electrical system to shutdown the lighting plant at a preset time of day |  |  |  |
| All cabling in the areas of the light fittings or ballast shall be constructed of high temperature 200 degree Celsius silicon 2.5mm2 cables |  |  |  |
| General |  |  |  |
| Electrical enclosures and panels must be locked or require a tool to gain access to live conductors. |  |  |  |
| Bushings on any cable that passes through a metallic structure |  |  |  |
| All Earth cable to be green and yellow |  |  |  |
| Supplied wiring diagram |  |  |  |
| All electrical enclosures shall be a minimum of IP56 except where otherwise stated |  |  |  |
| Confirm any electrical leads have test-tag in date (elec licence # must be legible) |  |  |  |

| Result of Inspection | Pass: | Yes No |  | Follow up inspection required: |  | Yes No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (Only issue sticker if both Elect & Mech inspections are done) | Mechanical inspection completed |  | Yes No N/A |  | Sticker Issued (circle) |  | Green Orange |
|  | Sticker number: |  |  | Expiry date |  |  |  |
| Comments or details of repairs needed |  |  |  |  |  |  |  |

I certify that this report is a true record of the equipment’s compliance.

Signature (Inspector):		Date: 		Location of Inspection: