| Equipment Owner or Responsible Person |  | Equipment Type/Make/Model/Shape |  | Call Sign/Equipment ID |  | Registration Number |
| --- | --- | --- | --- | --- | --- | --- |
| Company the inspection is conducted for |  | Inspected by (print) |  | Inspection Company |  |  |
| Declaration Submitted | Towing Capacity | Meter Reading | First Inspection |  | Annual Inspection |  |
| Yes No |  |  | Random Inspection |  | Re-Inspection |  |

|  | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Electrical Labelling |  |  |  |
| Maximum voltage above ELV within the enclosure Sign |  |  |  |
| Signs on any cover or door which exposes live conductors |  |  |  |
| Protection |  |  |  |
| The minimum degree of protection against access to live parts shall be IP2X |  |  |  |
| All electrical conductors terminated correctly, secured and effective as per AS3000 |  |  |  |
| Portable generators that are used on site to supply tools and appliances are required to have internal wiring that is in accordance with AS 3010 |  |  |  |
| The main AC electrical supply provided by the alternator shall be protected by a circuit breaker fitted with an adjustable 30-100mA Residual Current Device (RCD) with a testing facility |  |  |  |
| Each power circuit shall be protected by an individual circuit breaker with 30mA residual current protection. Any 240V AC power outlets shall be over current and earth leakage protected by individual circuit breakers with 30mA residual current devices |  |  |  |
| Lockable isolation of electrical energy when inspection, repair or maintenance is being carried out |  |  |  |
| Segregation of ELV and LV |  |  |  |
| The LV cables are double insulated |  |  |  |
| All cable or each conductor of a multi-core cable are insulated to the highest voltage |  |  |  |
| The LV cables are physically separated from the ELV cables by suitable continuous barriers |  |  |  |
| Generators |  |  |  |
| Portable generators used for the provision of general power shall be supplied with a “Stamford”, 37 KVA, 415 Volt, 3 phase, 50 Hz, double bearing, direct coupled, four poles, revolving field alternator or an agreed equivalent. The alternator shall be anti-vibration mounted. |  |  |  |
| Where portable generators are supplying an appliance onto metal framed equipment, and the generator and the equipment can be touched at the same time. Then equipotential bonding shall be required between the equipment and the generator |  |  |  |
| Alternative alternators to suit particular applications, shall be approved by the EEM. |  |  |  |
| Engine shall be fitted with a ‘Donaldson’ heavy-duty air cleaner and pre cleaner. |  |  |  |
| Engine shall be fitted with a Sound control muffler |  |  |  |
| Engine Protection |  |  |  |
| Low water protection |  |  |  |
| High temperature protection – Cat 7N9785 switch |  |  |  |
| Low oil pressure protection – Cat 107.0611 switch |  |  |  |
| PLC based controller |  |  |  |
| The 12 Volt electrical system |  |  |  |
| Circuit breakers in place of fuse holders |  |  |  |
| All wiring part of the 12V engine electrical system shall be protected by Adaptaflex PAF21 conduit. |  |  |  |
| Battery isolator switch with lockout device (LockSafe device, part number LS 11001-01) providing positive pole isolation |  |  |  |
| Emergency stop button to be mounted next to Wiggins fill point. |  |  |  |
| Two (2) fully adjustable rubber body 12 Volt sealed beam floodlights (Hella Matador with covers, Part Number 1511) for night work. |  |  |  |
| Control Panel |  |  |  |
| Shall be housed within a sealed box with clear hinged lid. |  |  |  |
| Key start ignition with lockout device |  |  |  |
| Hour meter |  |  |  |
| Electrical System |  |  |  |
| protected by a voltage regulator ensuring that the electrical system maintains 415V in 3 phase configuration and 240V in single phase configuration |  |  |  |
| One ammeter for monitoring current draw in each phase from the alternator |  |  |  |
| Three voltmeters for monitoring the voltage levels at the alternator |  |  |  |
| Can be fitted with: one 415V, 90A, 3 phase + N + E , weatherproof socket outlet, one 240V, 1 phase, 3 pin weatherproof socket outlet and one selector switch to change between each outlet. The selector switch shall provide interlocks on the outlet circuits to ensure only one socket is ever supplied at any time. |  |  |  |
| General |  |  |  |
| Electrical enclosures and panels must be locked or require a tool to gain access to live conductors. |  |  |  |
| Bushings on any cable that passes through a metallic structure |  |  |  |
| All Earth cable to be green and yellow |  |  |  |
| Supplied wiring diagram |  |  |  |
| All electrical enclosures shall be a minimum of IP56 except where otherwise stated |  |  |  |
| Confirm any electrical leads have test-tag in date (elec licence # must be legible) |  |  |  |

| Result of Inspection | Pass: | Yes No |  | Follow up inspection required: |  | Yes No |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (Only issue sticker if both Elect & Mech inspections are done) | Mechanical inspection completed |  | Yes No N/A |  | Sticker Issued (circle) |  | Green Orange |
|  | Sticker number: |  |  | Expiry date |  |  |  |
| Comments or details of repairs needed |  |  |  |  |  |  |  |

I certify that this report is a true record of the equipment’s compliance.

Signature (Inspector):		Date: 		Location of Inspection: