| Equipment Owner or Responsible Person |  | Equipment Type/Make/Model/Shape |  | Call Sign/Equipment ID |  | Registration Number |
| --- | --- | --- | --- | --- | --- | --- |
| Company the inspection is conducted for |  | Inspected by (print) |  | Inspection Company |  |  |
| Declaration Submitted | Towing Capacity | Meter Reading | First Inspection |  | Annual Inspection |  |
| Yes No |  |  | Random Inspection |  | Re-Inspection |  |

|  | Pass | Fail | N/A |
| --- | --- | --- | --- |
| Electrical Labelling |  |  |  |
| Maximum voltage above ELV within the enclosure Sign |  |  |  |
| Signs on any cover or door which exposes live conductors |  |  |  |
| All circuits, circuit breakers & fixtures will be clearly labelled as per “as-built” drawings |  |  |  |
| Protection |  |  |  |
| The minimum degree of protection against access to live parts shall be IP2X |  |  |  |
| All electrical conductors terminated correctly, secured and effective as per AS3000 |  |  |  |
| All circuits to be protected by a minimum of 30mA by earth leakage. |  |  |  |
| Main Circuit Breaker should have a fault rating capacity of 25KA and all sub-circuit breakers should be rated at 6KA as minimum requirement |  |  |  |
| All Circuit Breakers are to be Schneider manufacture, dual pole and use protection curve C |  |  |  |
| Lockable isolation of electrical energy when inspection, repair or maintenance is being carried out |  |  |  |
| Test that the Earth Leakage is functional and trips the relevant breaker |  |  |  |
| Overcurrent Protection |  |  |  |
| Segregation of ELV and LV |  |  |  |
| The LV cables are double insulated |  |  |  |
| All cable or each conductor of a multi-core cable are insulated to the highest voltage |  |  |  |
| The LV cables are physically separated from the ELV cables by suitable continuous barriers |  |  |  |
| Lighting |  |  |  |
| All Lighting to have a minimum Power Correction Factor (PCF) of 0.9 |  |  |  |
| Emergency evacuation lighting, when required, shall be sufficient to allow egress from the site |  |  |  |
| Air-conditioning |  |  |  |
| provide a suitable switch for the unit at the desired location of the Air Conditioner. It should be at a height of 1800mm above the floor. |  |  |  |
| Each A/C is to be fed individually from a Circuit Breaker of 30mA with E/L protection. As a rule of thumb, the 9000 & 12000 BTU are to be fed from a 10 Amp Circuit Breaker. And the 24000 BTU is to be fed from 16 Amp Circuit Breaker. The 30000 BTU units are to be assessed individually. |  |  |  |
| GPOs and Switches |  |  |  |
| Double-pole GPO units with neutral breaking capability shall be used |  |  |  |
| All switches that are installed in a relocatable premise that are intended to be connected to the site supply by means of a detachable connection shall operate in both active and neutral conductors |  |  |  |
| Any switches rated 20 Amps and above are required to have pad lockable facilities in the “off” position |  |  |  |
| All Light switches are to be double pole and IP66 rated |  |  |  |
| All lighting switch mechanisms nominated shall be able to switch the designed load |  |  |  |
| General |  |  |  |
| Electrical enclosures and panels that access live conductors must be locked or require a tool to gain access. |  |  |  |
| Glands on any cable that passes through a metallic structure |  |  |  |
| Cables are to exit/enter the switchboard through gland plates |  |  |  |
| Switchboard shall be made from steel with minimum thickness of 2.0mm |  |  |  |
| Switchboard shall be arranged so flow is left to right |  |  |  |
| Cabling are to be coloured as follow: 415V AC Power: red, white, blue 240V AC Power: red 415/240V Neutral: black 110V control: white Earth: green and yellow |  |  |  |
| Relevant Circuit Diagram |  |  |  |
| Confirm any electrical leads have test-tag in date (elec licence # must be legible) |  |  |  |
| Maximum height of switchboard is less than 2200mm |  |  |  |
| Switchboard is to be powder coated, orange is preferred. |  |  |  |

| Result of Inspection | Pass: | Yes No | Follow up inspection required: | Yes No |  |
| --- | --- | --- | --- | --- | --- |
|  | Sticker Issued (circle) | Green Orange | Sticker number: |  | Expiry date / / |
| Comments or details of repairs needed |  |  |  |  |  |

I certify that this report is a true record of the equipment’s compliance.

Signature (Inspector):		Date: 		Location of Inspection: